## Slide 1: EIT Progress Assessment 3
Presented by: Khutso Makena
Unique Number: 4542278
Date :19-Oct-2018
Mentor: Adesh Singh
Chief mentor: Sidwell Mtetwa

## Slide 2: Presentation Outline
Introduction
Outline of Training Schedule Completed
Eskom life saving rules
Elective-Line Engineering Services (LES)
Future work
Value added

## Slide 3: Introduction
Name | Khutso Makena
Degree | BEng. Electrical Engineering (Heavy Current)
University | UP
Mentor | Adesh Singh
Chief mentor | Sidwell Mtetwa

## Slide 4: Outline of Training Schedule Completed
Department | Duration
Lines Engineering Services (LES) | 5 months

## Slide 5: Eskom 5 Life Saving Rules
20 10-Oct-172017
5
5
RULE 1: OPEN, ISOLATE, TEST, EARTH, BOND and/or INSULATE BEFORE TOUCH
RULE 2: HOOK UP AT HEIGHTS
RULE 3: BUCKLE UP
RULE 4: BE SOBER
RULE 5: ENSURE THAT YOU HAVE A PERMIT TO WORK

## Slide 6: Line Engineering Services
Design and construction of overhead powerlines

## Slide 7: Project : 275kV Bypass design
The following is understood from report TRC-RP0001 complied by the Tx Central Grid:
Eiger substation is situated in Alberton
A plant condition criticality assessment (CCRA) was conducted at Eiger to evaluate the health of the existing asset base.
The objective of this project is to replace old and underrated equipment, based on the technical recommendation from the CCRA to improve the operational integrity of Eiger substation.
The listed feeder bays are involved as part of the Eiger refurbishment scheme:
- Brenner - Lethabo - Etna - Alberton 1 and 2

## Slide 8: Geographical Location
Affected Substations

## Slide 9: Alberton 1 and 2 Alternative solution

## Slide 10: Proposed bypass route 1

## Slide 11: Route 2

## Slide 12: Selection process
Route 2 was selected
Reasons:
  No need to equip the buscoupler bay (cost and time saving).
  Replacing strain woodpoles with suspension poles (cost saving).
  Only need 1 feeder to energize the underpass.
  Caters for future work.

## Slide 13: Line summary Eiger- 275 kV
LINE | LENGTH (Km) | CONDUCTOR BUNDLE | RATE A (MVA) | RATE B (MVA) | TEMPLATE TEMPERATURE
Eiger-Brenner | 43 | 4 x Zebra | 1353 | 1947 | 50°C
Eiger-Etna | 33 | 4 x Zebra | 1353 | 1947 | 50°C
Eiger-Fordsburg | 19 | 4 x Bear | 993 | 1461 | 50°C
Eiger-Prospect | 19 | 4 x Bear | 993 | 1461 | 50°C
Proposed bypass | 0.5 | 2 x Bull | 1445 | 2017 | 70°C

## Slide 14: Structures
Terminal
Inline Strain
Suspension

## Slide 15: Crossings and clearance checks
Ground clearance
Brenner
Lethabo
Etna
Buscoupler A

## Slide 16: Clearance results
Lines | A (m) | B (m) | C (m)
Brenner | 3.835 | 3.759 | 5.201
Lethabo | 5.988 | 5.026 | 6.319
Buscoupler A | 4.930 | 4.075 | 4.543
Etna | 8.499 | 7.8 | 8.7
Fordsburg | 6.039 | 5.785 | 6.173
Prosburg | 5.503 | 5.261 | 5.894
Clearance checks from the lines above to the bypass below. Criteria for the clearance checks were done as specified below:
A-The higher line at templating temperature and the lower line at cold (-5oC)
B-The higher line at templating temperature and the lower line at maximum swing
B-The higher line at moderate swing with the lower line at maximum swing

## Slide 17: Insulator selection
Eiger substation
  275kV bypass
Method:
  Nominal voltage
    Dry arcing distance (SANS 10280)
    BIL
    SIL
  Type of insulator
    Glass insulators
    Composite insulators
  Pollution level
    Specific creepage distance (IEC 60815)
  Conductor mechanical loading
    Insulator strength (IEC 60120)

## Slide 18: Insulator selection
Insulator Material | Long-Rod Composite
System Nominal Voltage | 132kV
Insulator strength | 210kN
Specific Creepage Distance [mm/kV] | 25
Dry Arcing Distance [mm] | ≥1450
End-fitting Size [mm] | 20
BIL [kV] | 550

## Slide 19: Future work/activities
The following activities will be performed in future:
HVDC project
Investigations on Minerva-Vulcan and Apollo-Thuso lines
Etna-Glockner 400kV Line

## Slide 20: Value added to me
20
Understating the importance of each department and how their contribution sustains the business.
Application of theoretical knowledge in practical situations
Improvement on communication and networking skills
The awareness of standards

## Slide 21: Value added to the business
21
During the past six months of training, I was given projects that provided me the platform to add value to the business.
  Grounding impedance measurement
  Insulator selection
  Masa-Ngwedi site visit
  Routine tests