## Slide 1: Diagnosis of Gassing Transformer using DGA
Presented by: Teboho Richard Lekeno
Date: 26 May 2020

## Slide 2: Presentation Outline/Overview
1. What is dissolved gas analysis?
2. Faults and generate gases
3. DGA methods to be used
3.1. Key-gas method
3.2. Individual and total dissolved key-gas concentration method
3.3. Rogers ratio method
3.4. Duval triangle method
4. Transformer samples data
5. Transformer fault detection
5.1. Key-gas method
5.2. Individual and total dissolved key-gas concentration method
6. Transformer fault analysis
6.1. Rogers ratio method
6.2. Duval triangle method
7. Critical Analysis
8. Conclusion

## Slide 3: Purpose
Detect incipient faults
Supervise suspect transformers
Fault explanation
Assuring health of new transformers
Gas Name | Symbol
Hydrogen | H2
Methane | CH4
Ethylene | C2H4
Ethane | C2H6
Acetylene | C2H2
Carbon monoxide | CO
Carbon dioxide | CO2
Nitrogen | N2
Oxygen | O2
Total dissolved combustible gases | All mentioned gases accept CO2 & O2
Working principle
Oil and cellulose
Decomposition gases generation
Normal (aging)
Abnormal (faults)
Dissolve Gas Analysis

## Slide 4
Detect presence of faults
Uses individual gases or key gases
Correlate DGA results with 4 sets of charts.
Key Gas Method
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
overheated oil | 2 | 16 | 0 | 19 | 63 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
overheated cellulose | 0 | 0 | 93 | 0 | 0 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
partial discharge in oil | 85 | 13 | 0 | 1 | 1 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
arcing in oil | 60 | 5 | 0 | 2 | 3 | 30

## Slide 5
Used for detecting faults
Independent & assumes no previous tests made
Uses the highest level individual gas or TDCG
TDCG = condition 3 but a specific gas = condition 4 then transformer = condition 4
status | H2 | CH4 | C2H2 | C2H4 | C2H6 | CO | CO2 | TDCG
Condition 1 | 100 | 120 | 35 | 50 | 65 | 350 | 2500 | 720
Condition 2 | 101-700 | 121-400 | 36-50 | 51-100 | 66-100 | 351-570 | 2500-4000 | 721-1920
Condition 3 | 701-1800 | 401-1000 | 51-80 | 101-200 | 101-150 | 571-1400 | 4001-10000 | 1921-4630
Condition 4 | >1800 | 1000 | >80 | >200 | >150 | >1400 | >10000 | >4630
Individual and Total Dissolved Key-Gas Concentration Method
status | Operation
Condition 1 | Satisfactory (investigate excessive gases)
Condition 2 | Possible fault (investigate excessive gases)
Condition 3 | Excessive decomposition of cellulose/oil (take frequent samples for testing)
Condition 4 | Excessive decomposition of cellulose/oil (continuing operation may lead to failure)

## Slide 6
Rogers Ratio Method
Code Range of Ratios | C2H2/C2H4 | CH4/H2 | C2H4/C2H6 | Detection limits |  | 
 |  |  |  | x1 | x10 | gas
< 0.1 0.1-1 1-3 >3 | 0 1 1 2 | 1 0 2 2 | 0 0 1 2 | 1 ppm 10 ppm C2H2 1 ppm 10 ppm C2H4 1 ppm 10 ppm CH4 1 ppm 10 ppm C2H6 5 ppm 50 ppm H2 |  | 
case | C2H2/C2H4 | CH4/H2 | C2H4/C2H6 | Suggested Fault Type |  | 
0 | 0 | 0 | 0 | No fault |  | 
1 | 1 | 1 | 0 | Low energy PD |  | 
2 | 1 | 1 | 0 | High energy PD |  | 
3 | 1-2 | 0 | 1-2 | Low energy arcing, sparking, discharge |  | 
4 | 1 | 0 | 2 | High energy discharge, arcing |  | 
5 | 0 | 0 | 1 | Thermal fault <150°C |  | 
6 | 0 | 2 | 0 | Thermal F 150-300°C |  | 
7 | 0 | 2 | 1 | Thermal F 300-700°C |  | 
8 | 0 | 2 | 2 | Thermal fault >700°C |  | 
Fault analyzing not fault detecting
Uses 3 ratios
Denominator = gas detection limit if gas (denominator) = 0
Derived from Doernenburg ratio method
Accuracy drops with gas used < 10x chromatograph can detect

## Slide 7
Duval Triangle Method
Fault analyzing not fault detecting
Uses 3 gases percentage contributions
The analysis depends on past results
Highly accurate
Fault is three lines intersection
Zone | Fault Indication
T1 | Thermal fault ≤ 300°C
T2 | Thermal fault > 300°C, ≤ 700°C
T3 | Thermal fault > 700°C
D1 | Low energy discharge (sparking)
D2 | High energy discharge (Arcing)
DT | Combination of thermal and electrical faults
PD | Partial discharge

## Slide 8
Requirements to us the DTM
A problem with the transformer should exist
One of the hydrocarbons or hydrogen should on condition 3 or
At least one individual gas must be at L1 level or above
ABB (and the gas generation rate at G2)
Duval Triangle Method Continue
Gas | L1 limit | G1 limits (ppm/month) | G2 limits (ppm/month)
H2 | 100 | 10 | 50
CH4 | 75 | 8 | 38
C2H2 | 3 | 3 | 3
C2H4 | 75 | 8 | 38
C2H6 | 75 | 8 | 38
CO | 700 | 70 | 350
CO2 | 7000 | 700 | 3500
method | % correct diagnosis | % unresolved diagnosis | % wrong diagnosis
KGM | 42 | 0 | 58
RRM | 62 | 33 | 5
DTM | 96 | 0 | 4

## Slide 9
Transformer Samples Data
Sample date | H2 | O2 | N2 | CH4 | CO | CO2 | C2H6 | C2H4 | C2H2 | Moisture reading
2013/11/07 | 84 | 9003 | 55661 | 26 | 86 | 136 | 51 | 11 | 0 | 1
2014/05/06 | 93 | 3014 | 43697 | 42 | 107 | 86 | 82 | 17 | 0 | 7
2014/11/04 | 75 | 2247 | 41555 | 49 | 119 | 389 | 96 | 20 | 0 | 3
2015/05/05 | 65 | 2801 | 49238 | 81 | 120 | 528 | 127 | 44 | 0 | 5
2015/11/04 | 49 | 2687 | 49813 | 100 | 123 | 618 | 146 | 62 | 0 | 5
2016/05/05 | 41 | 2560 | 54990 | 128 | 132 | 528 | 193 | 80 | 0 | 4
2016/11/02 | 42 | 2251 | 52823 | 135 | 128 | 625 | 188 | 90 | 0 | 7
2017/05/04 | 28 | 4576 | 57925 | 140 | 118 | 522 | 228 | 94 | 0 | 11
2017/11/01 | 35 | 3197 | 59794 | 177 | 175 | 754 | 243 | 104 | 0 | 8
2018/05/03 | 35 | 2593 | 58770 | 201 | 162 | 301 | 286 | 136 | 0 | 4

## Slide 10
Fault Detection Using Key-Gas Method
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2014/05/06 00:00 | 93 | 42 | 107 | 82 | 17 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2015/05/05 07:00 | 65 | 81 | 120 | 127 | 44 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2016/11/02 14:46 | 42 | 135 | 128 | 188 | 90 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2018/05/03 00:00 | 35 | 201 | 162 | 286 | 136 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2014/11/04 00:00 | 75 | 49 | 119 | 96 | 20 | 0
Chart: 
| H2 | CH4 | CO | C2H6 | C2H4 | C2H2
2013/11/07 00:00 | 84 | 26 | 86 | 51 | 11 | 0

## Slide 11
Fault Detection Using Individual & Total Dissolved Key-Gas Concentration Method
Sample date | H2 | O2 | N2 | CH4 | CO | CO2 | C2H6 | C2H4 | C2H2 |  | TDCG | 
2013/11/07 | 84 | 9003 | 55661 | 26 | 86 | 136 | 51 | 11 | 0 |  | 258 | 1.581
2014/05/06 | 93 | 3014 | 43697 | 42 | 107 | 86 | 82 | 17 | 0 |  | 341 | 0.804
2014/11/04 | 75 | 2247 | 41555 | 49 | 119 | 389 | 96 | 20 | 0 |  | 359 | 3.269
2015/05/05 | 65 | 2801 | 49238 | 81 | 120 | 528 | 127 | 44 | 0 |  | 437 | 4.400
2015/11/04 | 49 | 2687 | 49813 | 100 | 123 | 618 | 146 | 62 | 0 |  | 480 | 5.024
2016/05/05 | 41 | 2560 | 54990 | 128 | 132 | 528 | 193 | 80 | 0 |  | 574 | 4
2016/11/02 | 42 | 2251 | 52823 | 135 | 128 | 625 | 188 | 90 | 0 |  | 583 | 4.883
2017/05/04 | 28 | 4576 | 57925 | 140 | 118 | 522 | 228 | 94 | 0 |  | 608 | 4.424
2017/11/01 | 35 | 3197 | 59794 | 177 | 175 | 754 | 243 | 104 | 0 |  | 734 | 4.309
2018/05/03 | 35 | 2593 | 58770 | 201 | 162 | 301 | 286 | 136 | 0 |  | 820 | 1.858
Sample date | H2 | O2 | N2 | CH4 | CO | CO2 | C2H6 | C2H4 | C2H2 |  | TDCG | 
2013/11/07 | 84 | 9003 | 55661 | 26 | 86 | 136 | 51 | 11 | 0 |  | 258 | 1.581
2014/05/06 | 93 | 3014 | 43697 | 42 | 107 | 86 | 82 | 17 | 0 |  | 341 | 0.804
2014/11/04 | 75 | 2247 | 41555 | 49 | 119 | 389 | 96 | 20 | 0 |  | 359 | 3.269
2015/05/05 | 65 | 2801 | 49238 | 81 | 120 | 528 | 127 | 44 | 0 |  | 437 | 4.400
2015/11/04 | 49 | 2687 | 49813 | 100 | 123 | 618 | 146 | 62 | 0 |  | 480 | 5.024
2016/05/05 | 41 | 2560 | 54990 | 128 | 132 | 528 | 193 | 80 | 0 |  | 574 | 4
2016/11/02 | 42 | 2251 | 52823 | 135 | 128 | 625 | 188 | 90 | 0 |  | 583 | 4.883
2017/05/04 | 28 | 4576 | 57925 | 140 | 118 | 522 | 228 | 94 | 0 |  | 608 | 4.424
2017/11/01 | 35 | 3197 | 59794 | 177 | 175 | 754 | 243 | 104 | 0 |  | 734 | 4.309
2018/05/03 | 35 | 2593 | 58770 | 201 | 162 | 301 | 286 | 136 | 0 |  | 820 | 1.858

## Slide 12
Fault Detection Using Individual & Total Dissolved Key-Gas Concentration Method Continue
Sample date | Status
2013/11/07 | Condition 1: Operating satisfactorily
2014/05/06 | Condition 1: Operating satisfactorily (C2H6 should be investigated, exceed limits)
2014/11/04 | Condition 1: Operating satisfactorily (C2H6 should be investigated, exceed limits)
2015/05/05 | Condition 1: Operating satisfactorily (C2H6 should be investigated, exceed limits)
2015/11/04 | Condition 1: Operating satisfactorily (C2H6 & C2H4 should be investigated, exceed limits)
2016/05/05 | Condition 1: Operating satisfactorily (C2H6 & C2H4 should be investigated, exceed limits)
2016/11/02 | Condition 1: Operating satisfactorily (C2H6 & C2H4 should be investigated, exceed limits)
2017/05/04 | Condition 1: Operating satisfactorily (C2H6 & C2H4 should be investigated, exceed limits)
2017/11/01 | Condition 2: A fault may be present (C2H6 & C2H4 should be investigated, exceed limits)
2018/05/03 | Condition 2: A fault may be present (C2H6 & C2H4 should be investigated, exceed limits)

## Slide 13
Fault Analysis Using Rogers Ratio Method
Sample date | H2 | CH4 | C2H6 | C2H4 | C2H2 |  |  |  | 
2013/11/07 | 84 | 26 | 51 | 11 | 0 |  | - | - | -
2014/05/06 | 93 | 42 | 82 | 17 | 0 |  | 0 | 0.452 | 0.207
2014/11/04 | 75 | 49 | 96 | 20 | 0 |  | 0 | 0.653 | 0.208
2015/05/05 | 65 | 81 | 127 | 44 | 0 |  | 0 | 1.246 | 0.346
2015/11/04 | 49 | 100 | 146 | 62 | 0 |  | 0 | 2.041 | 0.425
2016/05/05 | 41 | 128 | 193 | 80 | 0 |  | 0 | 3.122 | 0.415
2016/11/02 | 42 | 135 | 188 | 90 | 0 |  | 0 | 3.214 | 0.479
2017/05/04 | 28 | 140 | 228 | 94 | 0 |  | 0 | 5 | 0.412
2017/11/01 | 35 | 177 | 243 | 104 | 0 |  | 0 | 5.057 | 0.428
2018/05/03 | 35 | 201 | 286 | 136 | 0 |  | 0 | 5.743 | 0.476
Sample date | H2 | CH4 | C2H6 | C2H4 | C2H2 |  |  |  | 
2013/11/07 | 84 | 26 | 51 | 11 | 0 |  | - | - | -
2014/05/06 | 93 | 42 | 82 | 17 | 0 |  | 0 | 0.452 | 0.207
2014/11/04 | 75 | 49 | 96 | 20 | 0 |  | 0 | 0.653 | 0.208
2015/05/05 | 65 | 81 | 127 | 44 | 0 |  | 0 | 1.246 | 0.346
2015/11/04 | 49 | 100 | 146 | 62 | 0 |  | 0 | 2.041 | 0.425
2016/05/05 | 41 | 128 | 193 | 80 | 0 |  | 0 | 3.122 | 0.415
2016/11/02 | 42 | 135 | 188 | 90 | 0 |  | 0 | 3.214 | 0.479
2017/05/04 | 28 | 140 | 228 | 94 | 0 |  | 0 | 5 | 0.412
2017/11/01 | 35 | 177 | 243 | 104 | 0 |  | 0 | 5.057 | 0.428
2018/05/03 | 35 | 201 | 286 | 136 | 0 |  | 0 | 5.743 | 0.476

## Slide 14
Fault Analysis Using Rogers Ratio Method Continue
Sample date | H2 | CH4 | C2H6 | C2H4 | C2H2 |  | Fault Type | Problem found
2013/11/07 | 84 | 26 | 51 | 11 | 0 |  | - | -
2014/05/06 | 93 | 42 | 82 | 17 | 0 |  | No fault | -
2014/11/04 | 75 | 49 | 96 | 20 | 0 |  | No fault | -
2015/05/05 | 65 | 81 | 127 | 44 | 0 |  | Thermal F 150-300°C | -This issue could be stray flux in the tank. -overheating of copper conductor from eddy current -This issue involves cellulose insulation, which will produce CO and CO2
2015/11/04 | 49 | 100 | 146 | 62 | 0 |  | Thermal F 150-300°C | 
2016/05/05 | 41 | 128 | 193 | 80 | 0 |  | Thermal F 150-300°C | 
2016/11/02 | 42 | 135 | 188 | 90 | 0 |  | Thermal F 150-300°C | 
2017/05/04 | 28 | 140 | 228 | 94 | 0 |  | Thermal F 150-300°C | 
2017/11/01 | 35 | 177 | 243 | 104 | 0 |  | Thermal F 150-300°C | 
2018/05/03 | 35 | 201 | 286 | 136 | 0 |  | Thermal F 150-300°C | 

## Slide 15
Fault Analysis Using Duval Triangle Method
Sample date | CH4 | C2H6 | C2H4 | C2H2 |  | ∆CH4 | ∆C2H4 | ∆C2H2 | %CH4 | %C2H4 | %C2H2
2013/11/07 | 26 | 51 | 11 | 0 |  | - | - | - | - | - | -
2014/05/06 | 42 | 82 | 17 | 0 |  | - | - | - | - | - | -
2014/11/04 | 49 | 96 | 20 | 0 |  | 7 | 3 | 0 | 70 | 30 | 0
2015/05/05 | 81 | 127 | 44 | 0 |  | 32 | 24 | 0 | 57.14 | 42.86 | 0
2015/11/04 | 100 | 146 | 62 | 0 |  | 19 | 18 | 0 | 51.35 | 48.65 | 0
2016/05/05 | 128 | 193 | 80 | 0 |  | 28 | 18 | 0 | 60.87 | 39.13 | 0
2016/11/02 | 135 | 188 | 90 | 0 |  | 7 | 10 | 0 | 41.18 | 58.82 | 0
2017/05/04 | 140 | 228 | 94 | 0 |  | 5 | 4 | 0 | 55.56 | 44.44 | 0
2017/11/01 | 177 | 243 | 104 | 0 |  | 37 | 10 | 0 | 78.72 | 21.28 | 0
2018/05/03 | 201 | 286 | 136 | 0 |  | 24 | 32 | 0 | 42.86 | 57.14 | 0

## Slide 16
Fault Analysis Using Duval Triangle Method Continue

## Slide 17
Fault Analysis Using Duval Triangle Method Continue
Sample date | CH4 | C2H6 | C2H4 | C2H2 |  | Fault level
2013/11/07 | 26 | 51 | 11 | 0 |  | 
2014/05/06 | 42 | 82 | 17 | 0 |  | 
2014/11/04 | 49 | 96 | 20 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2015/05/05 | 81 | 127 | 44 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2015/11/04 | 100 | 146 | 62 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2016/05/05 | 128 | 193 | 80 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2016/11/02 | 135 | 188 | 90 | 0 |  | T3: thermal fault > 700°C
2017/05/04 | 140 | 228 | 94 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2017/11/01 | 177 | 243 | 104 | 0 |  | T2: thermal fault > 300°C, ≤ 700°C
2018/05/03 | 201 | 286 | 136 | 0 |  | T3: thermal fault > 700°C

## Slide 18: Critical Analysis of Results
Both the analyzing methods results shows the transformer to experience the thermal fault.
This faults involve the cellulose insulation
According to IEC 60599-2007, if < 3, there is excessive paper degradation due to conductor overheating
Moisture reading also increasing (paper release OH when heated), this will further reduce the life of the transformer.
The transformer can continue service under guided operating procedures.
The root cause (factor causing the conductor to overheat) should be found and eliminated.

## Slide 19: Conclusion
Different DGA method for detecting and analyzing transformer faults for presented.
The gassing transformer data was presented and DGA analysis was used to identify the problem.
Both the analyzing method (RRM & DTM) results showed the thermal fault to be occurring inside the transformer.
The transformer can continue with service and root cause should be eliminated